## Initialization
Slack Bus Number | 150
Base MVA | 5
Base KV | 4.16
Slack Bus Voltage Magnitude Phase A | 1
Slack Bus Voltage Magnitude Phase B | 1
Slack Bus Voltage Magnitude Phase C | 1
Slack Bus Voltage Angle Phase A | 0
Slack Bus Voltage Angle Phase B | -120
Slack Bus Voltage Angle Phase C | 120
Loading Factor | 1
Bus Renumbering Mode | 1

## Buses
Node Number | Va Benchmark | Vb Benchmark | Vc Benchmark
150 | 1 | 1 | 1
149 | 1.0436 | 1.0437 | 1.0436
1 | 1.0311 | 1.0412 | 1.0348
2 | NaN | 1.041 | NaN
3 | NaN | NaN | 1.0331
4 | NaN | NaN | 1.0326
5 | NaN | NaN | 1.0318
6 | NaN | NaN | 1.0311
7 | 1.0218 | 1.0395 | 1.0291
8 | 1.0158 | 1.0382 | 1.0253
12 | NaN | 1.0379 | NaN
13 | 1.0079 | 1.036 | 1.0196
152 | 1.0078 | 1.036 | 1.0196
52 | 1.0018 | 1.0348 | 1.0164
53 | 0.9991 | 1.034 | 1.0148
54 | 0.9976 | 1.0334 | 1.0138
55 | 0.9974 | 1.0334 | 1.0139
56 | 0.9974 | 1.0332 | 1.014
57 | 0.9945 | 1.0306 | 1.0113
58 | NaN | 1.03 | NaN
59 | NaN | 1.0296 | NaN
60 | 0.988 | 1.0256 | 1.0052
160 | 0.988 | 1.0256 | 1.0052
67 | 1.0355 | 1.0311 | 1.0345
68 | 1.034 | NaN | NaN
69 | 1.0322 | NaN | NaN
70 | 1.031 | NaN | NaN
71 | 1.0303 | NaN | NaN
72 | 1.0359 | 1.0302 | 1.0343
73 | NaN | NaN | 1.0321
74 | NaN | NaN | 1.0303
75 | NaN | NaN | 1.0293
76 | 1.0358 | 1.0297 | 1.0349
77 | 1.037 | 1.0308 | 1.0358
78 | 1.0373 | 1.0312 | 1.036
79 | 1.037 | 1.0313 | 1.0359
80 | 1.0394 | 1.0329 | 1.0368
81 | 1.0415 | 1.0352 | 1.0374
82 | 1.0424 | 1.0364 | 1.0382
83 | 1.0436 | 1.0375 | 1.039
84 | NaN | NaN | 1.0348
85 | NaN | NaN | 1.0336
86 | 1.0349 | 1.0279 | 1.0364
87 | 1.0342 | 1.0272 | 1.0369
88 | 1.0342 | NaN | NaN
89 | 1.0338 | 1.027 | 1.0373
90 | NaN | 1.0269 | NaN
91 | 1.0336 | 1.0266 | 1.0376
92 | NaN | NaN | 1.0375
93 | 1.0333 | 1.0265 | 1.0377
94 | 1.0326 | NaN | NaN
95 | 1.0332 | 1.0261 | 1.0378
96 | NaN | 1.0258 | NaN
97 | 1.0345 | 1.0306 | 1.0338
197 | 1.0345 | 1.0306 | 1.0338
101 | 1.0337 | 1.0303 | 1.0332
102 | NaN | NaN | 1.0318
103 | NaN | NaN | 1.0301
104 | NaN | NaN | 1.0283
105 | 1.0323 | 1.0301 | 1.0335
106 | NaN | 1.029 | NaN
107 | NaN | 1.0275 | NaN
108 | 1.0309 | 1.0308 | 1.0334
109 | 1.0267 | NaN | NaN
110 | 1.0248 | NaN | NaN
111 | 1.024 | NaN | NaN
112 | 1.0241 | NaN | NaN
113 | 1.022 | NaN | NaN
114 | 1.0216 | NaN | NaN
300 | 1.0309 | 1.0308 | 1.0334
98 | 1.0343 | 1.0303 | 1.0336
99 | 1.0346 | 1.0295 | 1.0332
100 | 1.0348 | 1.0294 | 1.0328
450 | 1.0348 | 1.0294 | 1.0328
61 | 0.988 | 1.0256 | 1.0052
611 | 0.988 | 1.0256 | 1.0052
610 | 0.988 | 1.0256 | 1.0052
62 | 0.9872 | 1.0245 | 1.0032
63 | 0.9866 | 1.0236 | 1.0022
64 | 0.9863 | 1.0217 | 1
65 | 0.9856 | 1.0214 | 0.997
66 | 0.9858 | 1.0216 | 0.9955
18 | 0.9988 | 1.0319 | 1.0122
135 | 0.9988 | 1.0318 | 1.0122
35 | 0.996 | 1.0293 | 1.0112
36 | 0.9951 | 1.0288 | NaN
37 | 0.9943 | NaN | NaN
38 | NaN | 1.0282 | NaN
39 | NaN | 1.0278 | NaN
40 | 0.9945 | 1.0282 | 1.0101
41 | NaN | NaN | 1.0097
42 | 0.9929 | 1.027 | 1.0092
43 | NaN | 1.0257 | NaN
44 | 0.9918 | 1.0263 | 1.0084
45 | 0.9913 | NaN | NaN
46 | 0.9909 | NaN | NaN
47 | 0.9908 | 1.0253 | 1.0074
48 | 0.9905 | 1.025 | 1.0072
49 | 0.9905 | 1.0247 | 1.0071
50 | 0.9905 | 1.0247 | 1.0067
51 | 0.9903 | 1.0248 | 1.0067
151 | 0.9903 | 1.0248 | 1.0067
19 | 0.9975 | NaN | NaN
20 | 0.9967 | NaN | NaN
21 | 0.9983 | 1.032 | 1.0111
22 | NaN | 1.0305 | NaN
23 | 0.9979 | 1.0323 | 1.01
24 | NaN | NaN | 1.0085
25 | 0.9972 | 1.0328 | 1.0091
28 | 0.9968 | 1.033 | 1.0087
29 | 0.9967 | 1.0332 | 1.0083
30 | 0.9969 | 1.0331 | 1.0078
250 | 0.9969 | 1.0331 | 1.0078
26 | 0.997 | NaN | 1.0023
27 | 0.9966 | NaN | 1.0022
33 | 0.9953 | NaN | NaN
31 | NaN | NaN | 1.0017
32 | NaN | NaN | 1.0013
34 | NaN | NaN | 1.0187
15 | NaN | NaN | 1.0183
16 | NaN | NaN | 1.0173
17 | NaN | NaN | 1.0178
9 | 1.0144 | NaN | NaN
14 | 1.0063 | NaN | NaN
10 | 1.006 | NaN | NaN
11 | 1.0057 | NaN | NaN

## Lines
From Bus | To Bus | Length (ft) | Configuration | Base kV
1 | 2 | 175 | 10 | 4.16
1 | 3 | 250 | 11 | 4.16
1 | 7 | 300 | 1 | 4.16
3 | 4 | 200 | 11 | 4.16
3 | 5 | 325 | 11 | 4.16
5 | 6 | 250 | 11 | 4.16
7 | 8 | 200 | 1 | 4.16
8 | 12 | 225 | 10 | 4.16
8 | 9 | 225 | 9 | 4.16
8 | 13 | 300 | 1 | 4.16
9 | 14 | 425 | 9 | 4.16
13 | 34 | 150 | 11 | 4.16
13 | 18 | 825 | 2 | 4.16
14 | 11 | 250 | 9 | 4.16
14 | 10 | 250 | 9 | 4.16
15 | 16 | 375 | 11 | 4.16
15 | 17 | 350 | 11 | 4.16
18 | 19 | 250 | 9 | 4.16
18 | 21 | 300 | 2 | 4.16
19 | 20 | 325 | 9 | 4.16
21 | 22 | 525 | 10 | 4.16
21 | 23 | 250 | 2 | 4.16
23 | 24 | 550 | 11 | 4.16
23 | 25 | 275 | 2 | 4.16
25 | 26 | 350 | 7 | 4.16
25 | 28 | 200 | 2 | 4.16
26 | 27 | 275 | 7 | 4.16
26 | 31 | 225 | 11 | 4.16
27 | 33 | 500 | 9 | 4.16
28 | 29 | 300 | 2 | 4.16
29 | 30 | 350 | 2 | 4.16
30 | 250 | 200 | 2 | 4.16
31 | 32 | 300 | 11 | 4.16
34 | 15 | 100 | 11 | 4.16
35 | 36 | 650 | 8 | 4.16
35 | 40 | 250 | 1 | 4.16
36 | 37 | 300 | 9 | 4.16
36 | 38 | 250 | 10 | 4.16
38 | 39 | 325 | 10 | 4.16
40 | 41 | 325 | 11 | 4.16
40 | 42 | 250 | 1 | 4.16
42 | 43 | 500 | 10 | 4.16
42 | 44 | 200 | 1 | 4.16
44 | 45 | 200 | 9 | 4.16
44 | 47 | 250 | 1 | 4.16
45 | 46 | 300 | 9 | 4.16
47 | 48 | 150 | 4 | 4.16
47 | 49 | 250 | 4 | 4.16
49 | 50 | 250 | 4 | 4.16
50 | 51 | 250 | 4 | 4.16
51 | 151 | 500 | 4 | 4.16
52 | 53 | 200 | 1 | 4.16
53 | 54 | 125 | 1 | 4.16
54 | 55 | 275 | 1 | 4.16
54 | 57 | 350 | 3 | 4.16
55 | 56 | 275 | 1 | 4.16
57 | 58 | 250 | 10 | 4.16
57 | 60 | 750 | 3 | 4.16
58 | 59 | 250 | 10 | 4.16
60 | 61 | 550 | 5 | 4.16
60 | 62 | 250 | 12 | 4.16
62 | 63 | 175 | 12 | 4.16
63 | 64 | 350 | 12 | 4.16
64 | 65 | 425 | 12 | 4.16
65 | 66 | 325 | 12 | 4.16
67 | 68 | 200 | 9 | 4.16
67 | 72 | 275 | 3 | 4.16
67 | 97 | 250 | 3 | 4.16
68 | 69 | 275 | 9 | 4.16
69 | 70 | 325 | 9 | 4.16
70 | 71 | 275 | 9 | 4.16
72 | 73 | 275 | 11 | 4.16
72 | 76 | 200 | 3 | 4.16
73 | 74 | 350 | 11 | 4.16
74 | 75 | 400 | 11 | 4.16
76 | 77 | 400 | 6 | 4.16
76 | 86 | 700 | 3 | 4.16
77 | 78 | 100 | 6 | 4.16
78 | 79 | 225 | 6 | 4.16
78 | 80 | 475 | 6 | 4.16
80 | 81 | 475 | 6 | 4.16
81 | 82 | 250 | 6 | 4.16
81 | 84 | 675 | 11 | 4.16
82 | 83 | 250 | 6 | 4.16
84 | 85 | 475 | 11 | 4.16
86 | 87 | 450 | 6 | 4.16
87 | 88 | 175 | 9 | 4.16
87 | 89 | 275 | 6 | 4.16
89 | 90 | 225 | 10 | 4.16
89 | 91 | 225 | 6 | 4.16
91 | 92 | 300 | 11 | 4.16
91 | 93 | 225 | 6 | 4.16
93 | 94 | 275 | 9 | 4.16
93 | 95 | 300 | 6 | 4.16
95 | 96 | 200 | 10 | 4.16
97 | 98 | 275 | 3 | 4.16
98 | 99 | 550 | 3 | 4.16
99 | 100 | 300 | 3 | 4.16
100 | 450 | 800 | 3 | 4.16
101 | 102 | 225 | 11 | 4.16
101 | 105 | 275 | 3 | 4.16
102 | 103 | 325 | 11 | 4.16
103 | 104 | 700 | 11 | 4.16
105 | 106 | 225 | 10 | 4.16
105 | 108 | 325 | 3 | 4.16
106 | 107 | 575 | 10 | 4.16
108 | 109 | 450 | 9 | 4.16
108 | 300 | 1000 | 3 | 4.16
109 | 110 | 300 | 9 | 4.16
110 | 111 | 575 | 9 | 4.16
110 | 112 | 125 | 9 | 4.16
112 | 113 | 525 | 9 | 4.16
113 | 114 | 325 | 9 | 4.16
135 | 35 | 375 | 4 | 4.16
149 | 1 | 400 | 1 | 4.16
152 | 52 | 400 | 1 | 4.16
160 | 67 | 350 | 6 | 4.16
197 | 101 | 250 | 3 | 4.16

## Impedances
Conf | R11 | R12 | R13 | R22 | R23 | R33 | X11 | X12 | X13 | X22 | X23 | X33 | B11 | B12 | B13 | B22 | B23 | B33
1 | 0.4576 | 0.156 | 0.1535 | 0.4666 | 0.158 | 0.4615 | 1.078 | 0.5017 | 0.3849 | 1.0482 | 0.4236 | 1.0651 | 5.6765 | -1.8319 | -0.6982 | 5.9809 | -1.1645 | 5.3971
2 | 0.4666 | 0.158 | 0.156 | 0.4615 | 0.1535 | 0.4576 | 1.0482 | 0.4236 | 0.5017 | 1.0651 | 0.3849 | 1.078 | 5.9809 | -1.1645 | -1.8319 | 5.3971 | -0.6982 | 5.6765
3 | 0.4615 | 0.1535 | 0.158 | 0.4576 | 0.156 | 0.4666 | 1.0651 | 0.3849 | 0.4236 | 1.078 | 0.5017 | 1.0482 | 5.3971 | -0.6982 | -1.1645 | 5.6765 | -1.8319 | 5.9809
4 | 0.4615 | 0.158 | 0.1535 | 0.4666 | 0.156 | 0.4576 | 1.0651 | 0.4236 | 0.3849 | 1.0482 | 0.5017 | 1.078 | 5.3971 | -1.1645 | -0.6982 | 5.9809 | -1.8319 | 5.6765
5 | 0.4666 | 0.156 | 0.158 | 0.4576 | 0.1535 | 0.4615 | 1.0482 | 0.5017 | 0.4236 | 1.078 | 0.3849 | 1.0651 | 5.9809 | -1.8319 | -1.1645 | 5.6765 | -0.6982 | 5.3971
6 | 0.4576 | 0.1535 | 0.156 | 0.4615 | 0.158 | 0.4666 | 1.078 | 0.3849 | 0.5017 | 1.0651 | 0.4236 | 1.0482 | 5.6765 | -0.6982 | -1.8319 | 5.3971 | -1.1645 | 5.9809
7 | 0.4576 | 0 | 0.1535 | 0 | 0 | 0.4615 | 1.078 | 0 | 0.3849 | 0 | 0 | 1.0651 | 5.1154 | 0 | -1.0549 | 0 | 0 | 5.1704
8 | 0.4576 | 0.1535 | 0 | 0.4615 | 0 | 0 | 1.078 | 0.3849 | 0 | 1.0651 | 0 | 0 | 5.1154 | -1.0549 | 0 | 5.1704 | 0 | 0
9 | 1.3292 | 0 | 0 | 0 | 0 | 0 | 1.3475 | 0 | 0 | 0 | 0 | 0 | 4.5193 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 1.3292 | 0 | 0 | 0 | 0 | 0 | 1.3475 | 0 | 0 | 0 | 0 | 0 | 4.5193 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 1.3292 | 0 | 0 | 0 | 0 | 0 | 1.3475 | 0 | 0 | 0 | 0 | 0 | 4.5193
12 | 1.5209 | 0.5198 | 0.4924 | 1.5329 | 0.5198 | 1.5209 | 0.7521 | 0.2775 | 0.2157 | 0.7162 | 0.2775 | 0.7521 | 67.2242 | 0 | 0 | 67.2242 | 0 | 67.2242
13 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Loads
Node Number | Y=1, D=0 | P=0, I=1, Z=2 | Ph A (kW) | Ph A (kVAr) | Ph B (kW) | Ph B (kVAr) | Ph C (kW) | Ph C (kVAr)
1 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
2 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
4 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
5 | 1 | 1 | 0 | 0 | 0 | 0 | 20 | 10
6 | 1 | 2 | 0 | 0 | 0 | 0 | 40 | 20
7 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
9 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
10 | 1 | 1 | 20 | 10 | 0 | 0 | 0 | 0
11 | 1 | 2 | 40 | 20 | 0 | 0 | 0 | 0
12 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
16 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
17 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 10
19 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
20 | 1 | 1 | 40 | 20 | 0 | 0 | 0 | 0
22 | 1 | 2 | 0 | 0 | 40 | 20 | 0 | 0
24 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
28 | 1 | 1 | 40 | 20 | 0 | 0 | 0 | 0
29 | 1 | 2 | 40 | 20 | 0 | 0 | 0 | 0
30 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
31 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 10
32 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 10
33 | 1 | 1 | 40 | 20 | 0 | 0 | 0 | 0
34 | 1 | 2 | 0 | 0 | 0 | 0 | 40 | 20
35 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0
37 | 1 | 2 | 40 | 20 | 0 | 0 | 0 | 0
38 | 1 | 1 | 0 | 0 | 20 | 10 | 0 | 0
39 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
41 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 10
42 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
43 | 1 | 2 | 0 | 0 | 40 | 20 | 0 | 0
45 | 1 | 1 | 20 | 10 | 0 | 0 | 0 | 0
46 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
47 | 1 | 1 | 35 | 25 | 35 | 25 | 35 | 25
48 | 1 | 2 | 70 | 50 | 70 | 50 | 70 | 50
49 | 1 | 0 | 35 | 25 | 70 | 50 | 35 | 20
50 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
51 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
52 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
53 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
55 | 1 | 2 | 20 | 10 | 0 | 0 | 0 | 0
56 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
58 | 1 | 1 | 0 | 0 | 20 | 10 | 0 | 0
59 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
60 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
62 | 1 | 2 | 0 | 0 | 0 | 0 | 40 | 20
63 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
64 | 1 | 1 | 0 | 0 | 75 | 35 | 0 | 0
65 | 0 | 2 | 35 | 25 | 35 | 25 | 70 | 50
66 | 1 | 0 | 0 | 0 | 0 | 0 | 75 | 35
68 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
69 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
70 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
71 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
73 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
74 | 1 | 2 | 0 | 0 | 0 | 0 | 40 | 20
75 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
76 | 0 | 1 | 105 | 80 | 70 | 50 | 70 | 50
77 | 1 | 0 | 0 | 0 | 40 | 20 | 0 | 0
79 | 1 | 2 | 40 | 20 | 0 | 0 | 0 | 0
80 | 1 | 0 | 0 | 0 | 40 | 20 | 0 | 0
82 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
83 | 1 | 2 | 0 | 0 | 0 | 0 | 20 | 10
84 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 10
85 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
86 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
87 | 1 | 0 | 0 | 0 | 40 | 20 | 0 | 0
88 | 1 | 2 | 40 | 20 | 0 | 0 | 0 | 0
90 | 1 | 2 | 0 | 0 | 40 | 20 | 0 | 0
92 | 1 | 2 | 0 | 0 | 0 | 0 | 40 | 20
94 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
95 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
96 | 1 | 0 | 0 | 0 | 20 | 10 | 0 | 0
98 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
99 | 1 | 0 | 0 | 0 | 40 | 20 | 0 | 0
100 | 1 | 2 | 0 | 0 | 0 | 0 | 40 | 20
102 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 10
103 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
104 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 20
106 | 1 | 0 | 0 | 0 | 40 | 20 | 0 | 0
107 | 1 | 0 | 0 | 0 | 40 | 20 | 0 | 0
109 | 1 | 0 | 40 | 20 | 0 | 0 | 0 | 0
111 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0
112 | 1 | 1 | 20 | 10 | 0 | 0 | 0 | 0
113 | 1 | 2 | 40 | 20 | 0 | 0 | 0 | 0
114 | 1 | 0 | 20 | 10 | 0 | 0 | 0 | 0

## Capacitors
Node Number | Y=1, D=0 | P=0, I=1, Z=2 | Ph A (kVAr) | Ph B (kVAr) | Ph C (kVAr)
83 | 1 | 2 | 200 | 200 | 200
88 | 1 | 2 | 50 | 0 | 0
90 | 1 | 2 | 0 | 50 | 0
92 | 1 | 2 | 0 | 0 | 50

## DERs
Node Number | Y=1, D=0 | P=0, I=1, Z=2 | Ph A (kW) | Ph A (kVAr) | Ph B (kW) | Ph B (kVAr) | Ph C (kW) | Ph C (kVAr)

## Regulators
From Bus | To Bus | Tap A | Tap B | Tap C
150 | 149 | 7 | 7 | 7
9 | 14 | -1
25 | 26 | 0 |  | -1
160 | 67 | 8 | 1 | 5

## Switches
From Bus | To Bus | Base KV
13 | 152 | 4.16
18 | 135 | 4.16
60 | 160 | 4.16
61 | 611 | 4.16
97 | 197 | 4.16
150 | 149 | 4.16

## Transformers
From Bus | To Bus | Type (YgYg=0, YgD=1, DD=2,DYg=3, YD=4) | % R | % X | Base KV | Base MVA | Epsilon
611 | 610 | 0 | 1.27 | 2.72 | 4.16 | 0.15 | 1e-06